## Sheet1
	evp_air_m_dot	cnd_air_m_dot	T_evp_air_in	W_evp_air_in	RH_evp_air_in	T_cnd_air_in	W_cnd_air_in	RH_cnd_air_in	n_cmp	dT_sh	T_evp_air_out	W_evp_air_out	RH_evp_air_out	T_cnd_air_out	W_cnd_air_out	RH_cnd_air_out	evp_Q_dot	cnd_Q_dot	cmp_W_dot	rfg_m_dot	COP	EER	evp_eps	cnd_eps	T_evp	P_evp	T_cnd	P_cnd	dT_sc	T_suction_gas	P_suction_gas	h_suction_gas	T_discharge_gas	P_discharge_gas	h_discharge_gas	T_liquid	P_liquid	h_liquid	T_mixture	P_mixture	h_mixture	x_mixture	evp_air_dP	cnd_air_dP
0	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	2100	10	16,1204009906581	8,41336041595253	73,4853137322287	40,8803728982104	10,5898923051913	21,8160190924224	4,18786730980134	5,39161074180198	1,21229617691323	92,1467002877878	4,44743689246814	3,45449188866088	0,506263544268782	0,467562104562778	9,54699859619331	4,08370858946035	46,2577896118157	11,9824902839639	10,4808029554864	19,5469985961933	4,08370858907194	413,394702363287	81,1186248431495	11,9824902839639	460,756856659013	35,7769866563294	11,982490282308	250,116664336689	9,54699859619331	4,08370858946035	250,116664336689	19,4448666746825	22,5959600746053	52,2083873089314
1	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	2400	10	15,6860200061562	8,23879984656328	74,0085126182539	41,7119820803205	10,5898923051913	20,8777386828795	4,7058556502638	6,15337233345456	1,45104458140675	103,989052169657	4,24065008911651	3,24308137087118	0,529001164843176	0,420524352245214	8,91859204769258	3,99838185755558	49,3407043229988	12,9620139545209	13,4842678044247	18,9185920476926	3,99838185719917	413,013439602143	84,744118376754	12,9620139545209	463,247193868134	35,8564365185741	12,9620139519805	250,22341936257	8,91859204769258	3,99838185755558	250,22341936257	19,8983169306797	22,5303870774112	52,2995258144835
2	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	2700	10	15,5003727171714	8,16447797393045	74,2278433077886	42,3328686237163	10,5898923051913	20,2070875656366	4,86297945751985	6,7191823126996	1,85562306758234	109,385192145094	3,62098447151442	2,62067202250064	0,530605550170318	0,244461841313389	8,64478860646358	3,96163263592353	62,455736645045	17,8166909099678	24,8242952167207	18,6447886064636	3,96163263558026	412,847046006942	100,364645876971	17,8166909099678	473,917862926994	37,6314414283243	17,8166908939593	252,781383195505	8,64478860646358	3,96163263592353	252,781383195505	21,4041593596262	22,5016445388439	52,4334112353974
3	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	3000	10	14,7795503991885	7,88234247839547	75,0985103465089	42,897922833986	10,5898923051913	19,6179719313825	5,46656912479903	7,24364187690862	1,77137295285907	128,986967654976	4,08928106597602	3,08606333633793	0,536234669897202	0,564652331866589	7,58012966327641	3,8211815721033	46,7803267519921	12,144468211278	4,71746341852588	17,5801296632764	3,82118157180693	412,198486830107	82,1595286483543	12,144468211278	461,637145217129	42,0628633334662	12,1444682104898	259,468575547175	7,58012966327641	3,8211815721033	259,468575547175	25,5347234403307	22,3951424273122	52,9002463173453
4	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	3300	10	14,2204751558347	7,67523094399863	75,8423836930301	43,6687491166929	10,5898923051913	18,8455642642567	5,92225625050839	7,94787238072243	2,02563977050292	135,642190866703	3,92363563179308	2,92364730232267	0,542978238697913	0,461873148636181	6,81423568725734	3,722520728747	51,378078460988	13,6415197753132	12,5839838875737	16,8142356872573	3,72252072848056	411,730422766552	87,6940005696379	13,6415197753132	465,491742361796	38,7940945734144	13,6415197724167	254,551913184911	6,81423568725734	3,722520728747	254,551913184911	23,4509726690163	22,3070796603155	52,7600738936501
5	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	3600	10	13,7928507705748	7,51718794802559	76,3908623646946	44,258151350003	10,5898923051913	18,2782695146025	6,27025460686036	8,48794315987567	2,21681698297729	144,210616355094	3,82888764614026	2,82849448331053	0,545996803791325	0,456637731386985	6,18898295164223	3,6434309781768	52,6457021535359	14,0775784326604	13,6812827496011	16,1889829516422	3,64343097793265	411,347393969033	89,3440224058882	14,0775784326604	466,686878262189	38,9644194039348	14,0775784291982	254,798210507576	6,18898295164223	3,6434309781768	254,798210507576	23,9573879386835	22,2341591768527	52,8867940914167
6	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	3900	10	13,4976330549674	7,41028074798495	76,7788296742202	44,8142340019241	10,5898923051913	17,7608080769875	6,5081306002065	8,99563842156995	2,48742175124758	149,467193543447	3,61645081581286	2,61641621367278	0,548046805153216	0,378580910657998	5,75865360796331	3,58974894627344	57,8356017656649	15,9730594193597	19,1695112479588	15,7586536079633	3,5897489460436	411,08330359064	95,5815933130183	15,9730594193597	470,994231816174	38,6660905177061	15,973059411558	254,329306557921	5,75865360796331	3,58974894627344	254,329306557921	23,9753938677705	22,1860627458268	53,1643698097584
7	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	4200	10	13,051300073581	7,25071968279413	77,3668068327982	45,2147577093585	10,5898923051913	17,3984316316864	6,86544605983147	9,36691716108405	2,50236929496425	163,065453273584	3,74321934813297	2,74357828544629	0,548691231480674	0,527245498074255	5,06088037490849	3,50399312923328	51,3124225440737	13,6192141666206	9,46949790294889	15,0608803749085	3,50399312902498	410,654278974122	88,0380936496583	13,6192141666206	465,89914709912	41,8429246411248	13,619214164775	259,105487847904	5,06088037490849	3,50399312923328	259,105487847904	26,8478480269139	22,1201878480613	53,5037113430093
8	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	4500	10	12,6913457733271	7,12632404290979	77,869009839553	45,7113694391257	10,5898923051913	16,9607570880603	7,14906194606931	9,82187247442641	2,67288156880509	170,052519772796	3,67463810931858	2,67466468754367	0,550431811296623	0,517732421500107	4,52484622001896	3,4391873532948	52,4250755609227	14,0009416427429	10,6601375890966	14,524846220019	3,43918735310174	410,324031275584	89,4484831234352	14,0009416427429	466,908747929725	41,764937971826	14,0009416404699	258,980391706734	4,52484622001896	3,4391873532948	258,980391706734	27,0986505107251	22,0630600468915	53,5899002738551
9	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	4800	10	12,3391156606661	7,00733308980315	78,3758247232752	46,2262821170145	10,5898923051913	16,5201492851617	7,42366696644532	10,2924494475661	2,86852936744372	174,960250225631	3,58805789627949	2,58796965814608	0,552569901694958	0,480203345148161	4,01062622070725	3,37788566388712	54,9136848449734	14,8837881128796	14,2923556081331	14,0106262207073	3,37788566370768	410,006685134959	92,4816003847109	14,8837881128796	469,029838733809	40,6213292368403	14,8837881087529	257,251346399385	4,01062622070725	3,37788566388712	257,251346399385	26,5150603004386	22,0083699918981	53,5181874071647
10	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	5100	10	12,0622457734764	6,9154725736343	78,7830183677038	46,7060315518067	10,5898923051913	16,1213366495691	7,63772197767955	10,7300357131048	3,09216722865322	178,221742523294	3,47006966947847	2,47002228951444	0,554268633756126	0,426176022490034	3,60744018554232	3,33040924371614	58,7025299072402	16,3074923413316	19,2590589167179	13,6074401855423	3,33040924354675	409,757498342469	97,0737253173958	16,3074923413316	472,217902250003	39,4434709905223	16,3074923328679	255,475949106274	3,60744018554232	3,33040924371614	255,475949106274	25,844699478464	21,9564767468968	53,3950021753816
11	1500	3216,315	24	9,34030977105529	50	35	10,5898923051913	30	5400	10	11,7983221010252	6,82959721737117	79,182466657187	47,1046843054166	10,5898923051913	15,798275318732	7,83993343867111	11,0950345583494	3,25525558190181	183,669815411898	3,40834514501236	2,4083925951187	0,554989449821184	0,417960517928656	3,20568828582833	3,2836122716787	59,9494996070866	16,7977558586529	20,2515612057297	13,2056882858283	3,28361227151878	409,508882810694	98,6288756740431	16,7977558586529	473,313161529653	39,697938401357	16,7977558485782	255,84615792602	3,20568828582833	3,2836122716787	255,84615792602	26,2694211375816	21,9149708471404	53,5428421830591