## Sheet1
	evp_air_m_dot	cnd_air_m_dot	T_evp_air_in	W_evp_air_in	RH_evp_air_in	T_cnd_air_in	W_cnd_air_in	RH_cnd_air_in	n_cmp	dT_sh	T_evp_air_out	W_evp_air_out	RH_evp_air_out	T_cnd_air_out	W_cnd_air_out	RH_cnd_air_out	evp_Q_dot	cnd_Q_dot	cmp_W_dot	rfg_m_dot	COP	EER	evp_eps	cnd_eps	T_evp	P_evp	T_cnd	P_cnd	dT_sc	T_suction_gas	P_suction_gas	h_suction_gas	T_discharge_gas	P_discharge_gas	h_discharge_gas	T_liquid	P_liquid	h_liquid	T_mixture	P_mixture	h_mixture	x_mixture	evp_air_dP	cnd_air_dP
0	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	2100	5	16.04449524686129	8.685173446798885	76.19525237393077	40.83186424115604	10.589892305191341	21.872212250614297	4.0872946543194875	5.347552058391612	1.261839984236917	95.96244438105582	4.237900308433705	3.2391544929456577	0.574754861148737	0.3981135843416349	10.836952608394313	4.263208058770122	48.161932698889075	12.580658751006485	8.253743608814943	15.836952608394313	4.263208057339623	409.501595013719	78.31161969667028	12.580658751006485	456.8391130662471	39.90818909007413	12.580658749479575	256.2274307109545	10.836952608394313	4.263208058770122	256.2274307109545	21.835658432845793	22.599593099065956	52.48026217941163
1	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	2400	5
2	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	2700	5	15.000755916396315	8.173802865551538	76.73714855063326	42.351014175340026	10.589892305191341	20.187859398807824	5.070852523136074	6.740353763067769	1.6716471255671963	120.23637293156145	4.0321630444468	3.033446739792954	0.5755489133788037	0.4387791918530713	9.191230412829213	4.035232641549231	49.80763614659173	13.115448856474544	9.522837486333515	14.191230412829213	4.035232640408822	408.54263154266204	80.67403666599307	13.115448856474544	458.59345647454273	40.28479866025822	13.115448854593641	256.78036984013664	9.191230412829213	4.035232641549231	256.78036984013664	23.151956979065222	22.442027162111625	52.63319816798361
3	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	3000	5	14.550595994576383	7.9645238214800695	77.00183044013406	43.00803496187973	10.589892305191341	19.505459367401368	5.4828739592117826	7.342874739015168	1.8671158050534142	131.1385308201464	3.9327366407275974	2.9365473445043913	0.5751293000909453	0.4517200861715155	8.470964976209814	3.9384366235904014	50.53201155218585	13.356172979540382	9.562063729458544	13.470964976209814	3.938436622558509	408.12080860173654	81.72322545349516	13.356172979540382	459.37665885532095	40.969947822727306	13.356172977642563	257.8008985114085	8.470964976209814	3.9384366235904014	257.8008985114085	24.127038537810332	22.357350691409774	52.81787623058068
4	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	3300	5	14.133677319189928	7.778978651748846	77.28860191507236	43.61650613422768	10.589892305191341	18.896807249065606	5.855596534382359	7.900927667981232	2.056012636745736	141.38326239173082	3.8428400325821186	2.8480352842824046	0.5748642700704767	0.4623203488121766	7.8099795849514635	3.8511765065011776	51.18996242141333	13.577683367620878	9.480868317618956	12.809979584951463	3.851176505560175	407.73259130579436	82.67231237443758	13.577683367620878	460.0842301566272	41.70909410379437	13.577683365766747	258.90525660935936	7.8099795849514635	3.8511765065011776	258.90525660935936	25.103478321213196	22.285313202063715	53.04596030478396
5	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	3600	5	13.756205227593568	7.616553454855074	77.57307701481629	44.18797116573609	10.589892305191341	18.3447872686593	6.187070307806514	8.425041411040393	2.240354451168386	151.05128049089294	3.760584137321029	2.7616479635978326	0.57449959253445	0.4695263652296399	7.210766425570512	3.773354712456693	51.86728026223204	13.808583516782281	9.440252895547872	12.210766425570512	3.7733547115914674	407.3797492252025	83.61389332049976	13.808583516782281	460.7740402103249	42.42702736668417	13.80858351497867	259.9803165081677	7.210766425570512	3.773354712456693	259.9803165081677	26.022016555557016	22.220509149808645	53.20682720678262
6	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	3900	5	13.396080158986194	7.466429810333584	77.86761686608251	44.74033279143441	10.589892305191341	17.828606023235473	6.498117394470104	8.931287298579209	2.428064907065297	159.66522422293392	3.6783560738391015	2.676253577720092	0.5742117271123514	0.46557230055860477	6.639460099429016	3.7002820391974414	52.971543067146285	14.191338242220905	10.251562392524988	11.639460099429016	3.700282038399041	407.0425492207693	85.04902788921936	14.191338242220905	461.7885573635951	42.7199806746213	14.191338240155439	260.41324579298174	6.639460099429016	3.7002820391974414	260.41324579298174	26.5872182833185	22.16150995930268	53.331208360173186
7	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	4200	5	13.06361475178727	7.331306241948887	78.15369126470955	45.24113331502133	10.589892305191341	17.37486526146149	6.781526022836068	9.39056192058299	2.6008717228787974	168.1206462021521	3.610544048742613	2.6074050339283468	0.5735668444350951	0.4693905660650942	6.105732086334797	3.632998134068556	53.6232196898855	14.420926574227185	10.28710074510144	11.105732086334797	3.632998133328133	406.7268407700805	85.92549707761441	14.420926574227185	462.4198113473231	43.33611894478406	14.420926572202916	261.3378878728581	6.105732086334797	3.632998134068556	261.3378878728581	27.38094499558424	22.095931213217405	53.468357924644195
8	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	4500	5	12.760890010298226	7.212216547566116	78.43826008621168	45.688701110180034	10.589892305191341	16.98045981382311	7.035349441747185	9.801448908842449	2.75822620592447	176.6974156399129	3.5535333859817757	2.55067892061781	0.5728560102518988	0.48042184388439396	5.621603824406691	3.572780217024966	53.801275331104364	14.484138870952942	9.404672621123211	10.62160382440669	3.572780216333656	406.4399034652693	86.20388548234172	14.484138870952942	462.6354867756868	44.39660270998115	14.484138869358722	262.9426053373999	5.621603824406691	3.572780217024966	262.9426053373999	28.492076697108597	22.047115212145375	53.6197747914144
9	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	4800	5	12.477476642531485	7.103615354520255	78.72124321653389	46.111166876432435	10.589892305191341	16.617509201623808	7.2698765005437	10.189238300782057	2.913088197918	184.74951292374064	3.4977445269471628	2.495590935330939	0.5721392042412007	0.4869760681522328	5.167790622933239	3.517029502724883	54.114737788897116	14.595928238115734	8.765804558655248	10.16779062293324	3.5170295020767934	406.17044863960444	86.62119003916087	14.595928238115734	462.9344278595849	45.34893323024187	14.595928236839528	264.38853021515433	5.167790622933239	3.517029502724883	264.38853021515433	29.499556982608198	22.001244303066073	53.75397139250848
10	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	5100	5	12.154354821495133	6.983183091747003	79.06446821402189	46.585429690140586	10.589892305191341	16.220549558135932	7.533662137271717	10.623007747833292	3.091090980976286	190.13248240993042	3.436653211830774	2.437217857266788	0.5721961834875163	0.4688596244141226	4.659035509105024	3.4553237734974003	55.817228078136	15.214454755730365	11.20078447115958	9.659035509105024	3.4553237728947113	405.86782007181074	88.74225599486778	15.214454755730365	464.3950500877854	44.61644360697642	15.214454753494582	263.2572570738208	4.659035509105024	3.4553237734974003	263.2572570738208	29.21310464574888	21.95170094010626	53.805862096225724
11	1500.0	3216.315	24.0	9.340309771055281	50.0	35.0	10.589892305191341	30.0	5400	5	11.93416916929101	6.903133937709033	79.31113947320756	46.93822595051762	10.589892305191341	15.932264235113184	7.711213814791102	10.947565844431313	3.222039535937092	198.6003395598386	3.397713070347954	2.3932710101114223	0.5711662804768715	0.4851765615379478	4.302301119785682	3.412553377807137	55.44902542652824	15.079044957674002	9.287217841266795	9.302301119785682	3.4125533772344663	405.65527554992104	88.26683682732516	15.079044957674002	464.0607261905454	46.16180758526144	15.079044956379107	265.6157631693313	4.302301119785682	3.412553377807137	265.6157631693313	30.626743279241207	21.91642346395338	54.03950712564049